# Guide for preparing a Recycled Water Management Plan

## Water Supply (Safety and Reliability) Act 2008

This document is intended to be used as a template to assist recycled water providers in the preparation of a Recycled Water Management Plan (RWMP) in accordance with the Queensland Water Supply (Safety and Reliability) Act 2008 (the Act). Development and implementation of an RWMP is intended to ensure the safe use of recycled water.

This document has been adapted from a national template that was prepared based on the Australian Guidelines for Water Recycling (AGWR) and a review of the recycled water provisions relating to individual Australian state and territories.

This document provides a template for recycled water providers to document the process of planning and managing their recycled water scheme. The RWMP can be utilised for a range of different purposes, including scheme management, staff training and induction and meeting regulatory requirements.

The format of this document can therefore be altered to tailor the document’s purpose as well as a scheme's, organisation’s or other regulatory requirements.

It is important that it is completed in conjunction with the Queensland Recycled Water Management Plan and Validation Guideline. The RWMP must address all mandatory requirements contained in the guideline. This, and other regulatory guidelines under the Act, can be obtained from the Department’s website at www.dews.qld.gov.au.

### This page has intentionally been left blank

# Name of the Council / Recycled Water Provider

# Service Provider Number (If any)

# Recycled Water Management Plan

# Name of the Scheme

## Date (Month/Year)/ Version

### Document control/version/history

| Version/ revision number | Version/ revision date | Original prepared by | Reviewed by | Review date | Approved by | Approval date |
| --- | --- | --- | --- | --- | --- | --- |

# Contents

1.	Introduction	4

1.1.	Purpose	4

1.2.	Regulatory background	4

1.3.	Roles and responsibilities	4

2.	Commitment to responsible use and management of recycled water	6

2.1.	Endorsement	6

2.2.	Nominee contact details	6

2.3.	Recycled water policy statement	6

3.	Assessment of the recycled water system	8

3.1.	Risk assessment team	8

3.2.	Scheme description	8

3.2.1.	Source water characterisation	8

3.2.2.	Intended end uses	10

3.2.3.	System description	11

3.2.4.	Process flow diagram	11

3.2.5.	Operating environment	15

3.2.6.	Recycled water product	15

3.3.	Hazard identification and risk assessment	15

3.3.1.	Methodology	15

3.3.2.	Hazard identification	15

3.3.3.	Hazardous events	16

3.3.4.	Unmitigated risks	16

3.3.5.	Significant risks	16

3.3.6.	Uncertainty levels	16

3.3.7.	Control measures and residual risk	16

3.4.	Operational control	17

3.4.1.	Critical control points	17

3.4.2.	Critical limits	17

3.4.3.	Alert levels	17

4.	Scheme validation	25

4.1.	Validation program	26

4.1.1.	Validation of treatment processes	26

4.1.2.	Verification of final water quality	26

4.1.3.	Validation of critical limits, operational limits and corrective actions	27

4.1.4.	Validation report	27

4.2.	Revalidation	27

5.	Operational procedures and process control	27

5.1.	Operational procedures	27

5.2.	Source water monitoring	28

5.3.	Operational monitoring	28

5.4.	Operational corrective actions	28

5.4.1.	Communication systems	28

5.5.	Monitoring equipment	28

5.5.1.	Equipment maintenance	28

6.	Verification of recycled water quality and operational performance	28

6.1.	Recycled water quality monitoring	28

6.1.1.	Monitoring location(s)	28

6.1.2.	Monitoring parameters	29

6.1.3.	Monitoring frequency	29

6.1.4.	Sampling techniques	29

6.1.5.	Sample analysis	29

6.2.	Documentation and reliability	30

6.3.	Satisfaction of recycled water users	30

6.4.	Short-term evaluation of results	30

6.5.	Corrective responses	30

7.	Management of incidents and emergencies	30

7.1.	Communication	30

7.2.	Incident and emergency response protocols	30

7.2.1.	Continuous improvement of incident management	31

8.	Documentation management and reporting	31

8.1.	Management of documentation and records	31

8.2.	Document review	31

8.3.	Reporting	31

9.	Supporting programs	31

9.1.	Operator, contractor and end user awareness and training	31

9.1.1.	Operator, contractor and end user awareness and involvement	31

9.1.2.	Operator, contractor and end user training	32

9.2.	End user agreements	32

9.3.	Community involvement and awareness	32

9.3.1.	Consultation	32

9.3.2.	Communication and education	32

9.4.	Evaluation and audit	32

9.4.1.	Audit of recycled water quality management	32

9.5.	Review and continuous improvement	33

10.	References	33

11.	Appendices	33

# 1.	Introduction

This section should describe the context of the RWMP and include relevant background information and a brief summary of the scheme.

## 1.1.	Purpose

Describe the purpose and scope of the RWMP including why and by whom the RWMP has been prepared.

## 1.2.	Regulatory background

Identify the regulatory and management framework relevant to the scheme, including the applicable legislation, standards, codes or guidelines that underpin the RWMP.

## 1.3.	Roles and responsibilities

Identify the entities directly involved in the scheme and their area of responsibility.

This section should include contact details for the responsible entities, particularly in the case of multiple entity schemes, including:

- recycled water provider(s)

- scheme manager (if applicable)

- scheme operator responsible for operation and maintenance of RWTP

- distributer(s)

- recycled water user(s).

| Example: Introduction This RWMP has been prepared by Northwood Regional Council (NRC) to meet obligations under the Queensland Water Supply (Safety and Reliability) Act 2008 in relation to the operation of the Newtown recycled water scheme. The Newtown recycled water scheme uses treated effluent from the Newtown WWTP, owned and operated by NRC, which has been in operation in its current form since July 2007, when plant upgrades were completed. Secondary treated Class C recycled water is supplied to the Newtown golf course for irrigation and used by NRC for irrigation of a sporting field. Remaining effluent undergoes further treatment to Class A+ standard, and is supplied to a neighbouring property for irrigation of minimally processed food crops (pears and nectarines). Regulatory Framework Responsibility for the management of water is largely vested in the state. Regulation of recycled water in Queensland encompasses a range of legislation and guidelines for the protection of public health and safety and environmental values. This RWMP addresses recycled water provisions of the Water Supply (Safety and Reliability) Act 2008, which primarily deal with the management of risks to public health arising from operation of the scheme. It incorporates regulatory requirements in accordance with: |
| --- |
| Water Supply (Safety and Reliability) Act 2008 | Regulates the management of recycled water production and supply to protect public health and ensure continuity of critical supplies |
| Associated regulatory guidelines | Contain specific requirements for meeting provisions under the Act, including requirements for developing RWMPs and scheme validation, water quality standards and auditing and reporting |
| Public Health Act 2005 | Contains provisions to ensure recycled water providers supply recycled water that is fit for use. An authorised person under the Act may obtain information or issue improvement notices where it is believed this requirement is not being met |
| Public Health Regulation 2005 | Sets public health water quality criteria for classes of recycled water sourced from sewage and required standards for certain applications, including the irrigation of minimally processed food crops |
| Other legislation relevant to the operation and management of the scheme, which is not specifically addressed in this document include: Environmental Protection Act 1994 Plumbing and Drainage Act 2002 Workplace Health and Safety Act 1995 In addition, scheme management is guided by other non-regulatory guidelines and standards, including the Australian Guidelines for Water Recycling and the WSAA National Wastewater Source Management Guidelines, which are recognised industry best-practice documents. Roles and Responsibilities NRC is responsible for both the sewerage network for the collection and supply of wastewater to the WWTP, and the WWTP itself, which produces recycled water for the scheme. NRC has signed recycled water supply agreements with each third party user that define in detail the terms of supply and roles and responsibilities of NRC as a recycled water provider and the recycled water user. Copies of supply agreements are provided in Appendix A. In general terms, NRC, as a recycled water provider, is responsible for: the production and supply of recycled water that is fit for purpose, ensuring that water quality complies with regulated standards and supply agreements up to designated transfer points defined in the RWMP and supply agreements implementation of communication and reporting protocols in the event that water quality does not meet required standards operation and maintenance of infrastructure for the production and supply of recycled water up to designated transfer points compliance with relevant regulatory requirements for recycled water ceasing supply of recycled water to a user if NRC becomes aware that recycled water is being used in a manner or for purposes other than that for which it is being supplied. Recycled water users are responsible for: using recycled water only in the manner and for the purposes for which it has been supplied, in accordance with supply agreements operation and maintenance of recycled water infrastructure after the designated transfer point implementation of control measures and compliance with usage restrictions defined in supply agreements. Responsible entity Business Entity: Northwood Regional Council ABN: 123321 Address: 1 West Street Northwood QLD 4444 Phone (business): 07 3213 2132 Mobile: 0432 132 132 Fax: 07 3213 2133 Email: info@northwoodrc.qld.gov.au |

# 2.	Commitment to responsible use and management of recycled water

## 2.1.	Endorsement

The RWMP should be signed and endorsed by an authorised representative of the recycled water provider or scheme manager (e.g. CEO or responsible personnel).

| Service provider name: |  |
| --- | --- |
| Service provider register number (if applicable): |  |
| Scheme name: |  |
| Statement of endorsement: I, <<insert name>> hereby endorse the enclosed recycled water management plan (RWMP) for the <<insert name of recycled water scheme>> recycled water scheme. |
| Endorsed by: | Name |
|  | Position (e.g. CEO) |
|  | Signature Date |

## 2.2.	Nominee contact details

The person (nominee) that will be the primary contact responsible for the RWMP and scheme is:

| Name: |  |
| --- | --- |
| Position: |  |
| Business entity: |  |
| Address: |  |
| Telephone number: |  | Mobile: |  |
| Email address: |  |

## 2.3.	Recycled water policy statement

Include a policy statement that documents the commitment of the organisation's senior management to responsible, safe and sustainable management of recycled water. The policy statement should outline the broad principles that guide the development of more detailed guidelines and procedures for operation and management of the scheme. An example of a recycled water policy statement from the Australian Guidelines for Water Recycling (AGWR) is provided below.

Example: Policy for a recycled water scheme The organisation or partnership supports and promotes the responsible use of recycled water and the application of a management approach that consistently meets the Australian Guidelines for Water Recycling, as well as recycled water user and regulatory requirements. To achieve this we will: ensure that protection of public and environmental health is recognised as being of paramount importance maintain communication and partnerships with all relevant agencies involved in management of water resources, including waters that can be recycled engage appropriate scientific expertise in developing recycled water schemes recognise the importance of community participation in decision-making processes and the need to ensure that community expectations are met manage recycled water quality at all points along the delivery chain from source to the recycled water user use a risk-based approach in which potential threats to water quality are identified and controlled integrate the needs and expectations of our users of recycled water, communities and other stakeholders, regulators and employees into planning processes establish regular monitoring of control measures and recycled water quality and establish effective reporting mechanisms to provide relevant and timely information, and promote confidence in the recycled water supply and its management develop appropriate contingency planning and incident-response capability participate in and support appropriate research and development activities to ensure continuous improvement and continued understanding of recycled water issues and performance contribute to the development of industry regulations and guidelines, and other standards relevant to public health and the water cycle continually improve our practices by assessing performance against corporate commitments and stakeholder expectations. The organisation or partnership will implement and maintain recycled water management systems consistent with the Australian Guidelines for Water Recycling to effectively manage the risks to public and environmental health. All managers and employees involved in the supply of recycled water are responsible for understanding, implementing, maintaining and continuously improving the recycled water management system. Membership and participation in professional associations dealing with management and use of recycled water is encouraged. Signed by responsible officer(s) Dated

# 3.	Assessment of the recycled water system

This section should provide detailed information and analysis pertaining to the entire recycled water supply scheme, from source to the end use or receiving environment, to enable implementation of appropriate preventive measures for the mitigation of significant hazards identified within the system.

## 3.1.	Risk assessment team

The risk assessment team, also known as the analysis team or HACCP team, will be primarily responsible for undertaking the hazard identification and risk assessment process, and is also likely to be involved in the development and implementation of various other elements of the RWMP. The members of this team will also form the basis of the team that undertakes ongoing regular reviews of the RWMP. Members should include suitably experienced representatives from different areas of the scheme such as management, operation and use, and may also include external regulators. At least one member should have formal risk assessment training or equivalent experience or skills.

Provide a summary of the risk assessment team members, including their position within the organisation or scheme and their area of expertise or role within the team. Copies or details of relevant qualifications or experience, such as HACCP certification should be attached.

| Example: Composition of risk assessment team |
| --- |
| Name | Position in company | Area of expertise |
| Joe Johnson (Team leader) | Risk analyst | Risk assessment (HACCP certified)* |
| Rebecca Rose | Manager, Water and sewerage services | Project management |
| Gale Gilles | Principal Process engineer | Treatment processes, operations and maintenance |
| Sean Smith | Treatment Plant supervisor | Treatment plant process and operations |
| Dale Davidson | Laboratory supervisor | Laboratory testing, quality assurance |
| Barry Bloggs | Water Quality Officer | Water quality and treatment, quality control |
| Mary Martin | Trade Waste Officer | Source control |
| Chris Collins | Property owner (end user) | Farm management |
| Dr Jane Jones | Public Health Officer, Health Department | Public health, virology |
| * Appendix B contains a copy of the certification for HACCP |

## 3.2.	Scheme description

The scheme description documents the details and characteristics of the main components of the scheme, which will form the basis for the risk assessment process.

### 3.2.1.	Source water characterisation

The source of the recycled water will significantly influence the potential hazards relevant to the scheme. Consideration of the source water catchment is important in identifying parameters that may be of concern. The depth of analysis required and significance of particular parameters will depend on the means and level of exposure associated with the end uses.

Include details of the source water characterisation for the scheme. This should include a description of the methodology used to characterise the source water and demonstrate that the methodology used is suitable to identify hazards and variability in the source water. The results should be presented including all analyses of data and assessment of temporal and spatial variation.

Note:	Refer to section 3.3.1 of the RWMP and Validation Guideline

| Example: Source water characterisation Characterisation of source water for the scheme involved conducting a land use analysis of the sewage catchment to identify potential sources of hazards in the catchment and analysis of existing source water monitoring data to support assumptions inferred from the land use analysis. The Newtown recycled water scheme uses treated effluent from the Newtown Wastewater Treatment Plant (WWTP), owned and operated by NRC. Influent for the treatment plant is collected within the Newtown catchment area, shown in Appendix B, with minor contributions from septage delivered by tanker to the inlet works. The wastewater influent into the WWTP is predominantly of domestic origin (96%), with the remainder contributed from commercial (3%) and industrial (1%) sources. The major industrial waste generators are an abattoir and leather tannery. Influent flow to the WWTP displays diurnal variability typical of domestic sewage systems, with peak flows in early morning and evening. Influent volume varies significantly throughout the year, largely in response to rainfall. Average monthly influent volume for 2010 is shown in Appendix C. Source water sampling is undertaken monthly and analysed by the NRC NATA accredited laboratory for the following parameters: |
| --- |
| pH | NOx |
| Suspended solids | TKN |
| COD | Organic N |
| BOD | Total N |
| Ammonia | Total P |
| Results of monthly source water monitoring for 2010 are provided in Appendix C, and summarised in Table 2 below. Results are consistent with a typical domestic sewage catchment. Microorganism density in raw sewage has been generally well characterised and is not routinely monitored by NRC. Table 2: Summary of source water monitoring results, 2010 |
| Parameter | Number of samples | Minimum | Maximum | Mean |
| pH |  |  |  |  |
| Suspended solids |  |  |  |  |
| COD |  |  |  |  |
| BOD |  |  |  |  |
| Ammonia |  |  |  |  |
| NOx |  |  |  |  |
| TKN |  |  |  |  |
| Organic N |  |  |  |  |
| Total N |  |  |  |  |
| Total P |  |  |  |  |
| Based on the low proportion of input from heavy industry and regulation of trade waste disposal, hazards associated with industrial waste generators are considered likely to pose relatively small additional risk to public health. Influent is screened quarterly for a range of metals, pesticides and pharmaceuticals. Results of quarterly testing for 2010 are also shown in Appendix C, and confirm that industrial hazards are low, generally close to or below Australian Drinking Water Guideline health values. |

### 3.2.2.	Intended end uses

The intent of a risk management approach is to protect public (and where relevant, environmental) health by ensuring that recycled water supplied is fit for use. The appropriate water quality is determined by the level of exposure based on how the recycled water is intended to be used, including control measures in place for minimising exposure.

Identify and describe the end uses for the scheme, including intended uses, control measures, potential routes of exposure, receiving environments, endpoints and effects. Also consider potential misuse, either accidental or intentional.

| Example: Intended end uses The Newtown WWTP produces two classes of recycled water that meet required standards for class C recycled water (secondary treated) and class A+ (tertiary treated). Recycled water is supplied for the following uses: |
| --- |
| Intended use | Potential misuse | Routes of exposure | Receiving environments/ endpoints | On-site control measures |
| Class C |
| Irrigation of council-owned football field via above ground sprinkler system | Person drinking from recycled water tap (accidental or intentional) | Skin contact Accidental ingestion of water or spray | Soil Plants Groundwater Wildlife | Irrigation timing – 10pm – 1am No use during irrigation and for at least 4 hours after irrigation, or until dry Use of low-throw sprinklers to minimise spray drift Vegetation screening along road boundaries Signage Locked valves on recycled water taps |
| Irrigation of golf course via above ground sprinkler system | Person drinking from recycled water tap (accidental or intentional) | Skin contact Accidental ingestion of water or spray | Soil Plants Groundwater Surface water ponds Wildlife | Fully fenced, locked after hours No access for 4 hours after irrigation, or until dry Use of low-throw sprinklers to minimise spray drift Signage Locked valves on recycled water taps |
| Class A |
| Irrigation of minimally processed food crops (pears, peaches) – spray irrigation 1-2 hours per day | Cross-connection with potable supply Person drinking from recycled water tap (accidental or intentional) | Ingestion of crops Skin contact Accidental ingestion of water or spray | Soil Crops Groundwater Surface water Humans Wildlife | Signage property boundaries and irrigation areas Purple pipes/taps, labelling Employees/ visitors informed of recycled water use and hygiene requirements No irrigation buffer zone within 25m of boundaries |
| Recycled water supply agreements are n place between NRC and both third party users. These are attached in Appendix A. |

### 3.2.3.	System description

This section should contain a comprehensive description of the scheme infrastructure and operation that demonstrates that scheme components are sufficiently well understood and documented to facilitate effective management. The level of detail required will depend on the complexity of the scheme and the purpose of the RWMP. A description of the nominated point of supply must be included. This is the point where the final water quality is monitored and must be representative of the water supplied to users under the scheme, ideally as close as possible to the physical point of transfer to users.

Document the infrastructure and processes used in the production and supply of the recycled water, including:

- collection network and the infrastructure used to collect the source water

- treatment system components, including process steps, pump stations, linkages, bypasses, dosing points and inputs to the system

- recycled water storages, including capacity, bypasses and overflow systems

- distribution system, including how and where recycled water is transferred to the users, and the control mechanisms in place

- nominated point of supply and documentation demonstrating that the water quality at this point is representative of the quality of water supplied to the user, particularly where the point of supply cannot be nominated at the physical transfer point.

### 3.2.4.	Process flow diagram

Information in the system description should be represented in a process flow (schematic) diagram. Diagrams are useful tools for visualising and consolidating technical details and systems, assisting the risk assessment process, identification of critical control points and communication.

Provide a process flow diagram that clearly depicts the recycled water system from source to end use and enables the nature of the scheme and relationships between components to be easily understood. This may be in the form of a series of connected flow diagrams and may include a simplified scheme diagram for risk assessment or critical control point identification purposes.

Example: System Description Influent to the Newtown WWTP consists primarily of raw sewage from the Newtown municipal sewerage system. A small proportion comes from septic tank waste delivered by tankers to the inlet works. The treatment plant uses a Modified Ludzack-Ettinger (MLE) system with chlorine disinfection. Effluent being treated to class A+ standard undergoes additional ultrafiltration and ultraviolet (UV) disinfection prior to chlorination. A flow diagram of the main system processes is provided in Figure 1. Sewage Catchment The Newtown sewerage system collects waste from the Newtown municipal area. The catchment area is shown in Appendix C. Balance Tank To moderate the impact of large fluctuations in influent volumes due to diurnal flow patterns, raw sewage is stored in the balance tank during peak flow periods. Flow of influent into the balance tank is controlled by an actuated valve that is automatically opened from 7am -10am, and 6pm-8pm. At other times influent bypasses the balance tank and is pumped directly to the inlet works. A valve at the outlet of the balance tank is opened between 11pm and 6am to release stored influent to the inlet works. A level indicator monitors stored influent levels in the balance tank, and the outlet valve also opens when the balance tank reaches 80% capacity. Inlet Works: Screening and Grit removal Influent, including raw sewage, septage and recycled process waters, enters the inlet works, which consists of two mechanical step screens (1 duty and 1 standby) to remove gross solids, and two grit channels. Dewatered solids are removed to industrial waste bins and transported to a licensed waste disposal facility. Influent flow to the inlet works is monitored, and in the event of overload in extreme wet weather, influent is diverted to an emergency bypass line to a holding tank. Wastewater in the emergency storage is returned to the bioreactor feed when influent flow is reduced. In the case of prolonged wet weather events, where emergency storage capacity is reached, wastewater is released to the environment (Eastern Creek). Bioreactor Primary treated wastewater from the inlet works is gravity fed into the anoxic chamber of the bioreactor, where it is mixed by a submersible mixer. Wastewater initially enters the anoxic chamber to provide a carbon source for the denitrification process. From the anoxic chamber, wastewater flows into the aerobic chamber, where ammonia is oxidised to nitrates by nitrifying bacteria. Oxygen levels in the aerobic chamber are maintained by diffusers, and dissolved oxygen in the chamber is continuously monitored. Ammonia levels are monitored online at the outlet of the bioreactor as an indicator of treatment efficiency. A proportion of the mixed liquor from the aerobic chamber is pumped through the recycle line and returned to the anoxic chamber to allow denitrification of nitrates produced in the aerobic chamber to nitrogen gas. Clarification Remaining effluent from the aerobic chamber of the bioreactor, that is not recycled to the anoxic chamber, flows into the clarifier. Alum is dosed to the clarifier as a flocculating agent and to assist phosphorous removal. Thickened activated sludge collected in the clarifier sump is pumped into two streams. Return Activated Sludge (RAS) is returned to the feed to the anoxic chamber of the bioreactor to re-seed the bioreactor. The remainder, the Waste Activated Sludge (WAS) is pumped to the aerobic sludge digester, then to a belt filter press for dewatering. Supernatant from the digestion and dewatering processes is returned to the bioreactor feed. Turbidity of clarified effluent is monitored online. The majority of the effluent, which is to be treated to class C, flows to Chlorine Contact Tank 1 (CCT1). The remainder that is to be treated to class A+ standards is pumped to the ultrafiltration units. Disinfection and Storage (Class C) Clarified effluent being treated to class C flows under gravity into CCT1. Sodium hypochlorite is dosed at the tank feed. Flow rate is monitored at entry and exit of the contact tank to regulate contact time. Free chlorine residual is also monitored online at the tank outfall. The chlorinated recycled water drains to the Class C storage tank. Free chlorine residual is monitored at the outfall of the storage tank to ensure adequate residual is maintained to prevent deterioration in water quality. The outfall of the storage tank is the nominated point of supply to Class C users and the location of final water quality monitoring for Class C recycled water. Fine Screen Prior to ultrafiltration, clarified effluent to be treated to class A+ standard passes through a fine screen to further remove particulate matter and protect the ultrafiltration membranes. Ultrafiltration From the fine screens, effluent enters one of four parallel ultrafiltration skids. Sodium hypochlorite is dosed at the feed to the ultrafiltration system to prevent membrane fouling. Only three units are in operation at a time, and the other on standby on a rotational basis. The membranes are backwashed every 30-45 minutes, and chemically cleaned every 2-3 weeks. Spent backwash water is returned to the bioreactor. UV Disinfection Effluent from the ultrafiltration unit is pumped to the UV system, which consists of 3 in-line units, providing a minimum dose of 60mJ/cm2. Chlorine Disinfection and Storage (Class A+) UV treated effluent flows into Chlorine Contact Tank 2 (CCT2). Sodium hypochlorite is dosed at the tank feed. Flow rate is monitored at entry and exit of the contact tank to regulate contact time. Free chlorine residual is also monitored online at the tank outfall. The chlorinated recycled water drains to the Class A+ storage tank. Free chlorine residual is monitored at the outfall of the storage tank to ensure adequate residual is maintained to prevent deterioration in water quality. From the outfall of the Class A+ storage tank, recycled water is pumped 1250m to the property boundary of the user. Final water quality monitoring of Class A+ recycled water is undertaken at the outfall of the storage tank (nominated point of supply for Class A+). Quarterly monitoring takes place just before the property boundary to demonstrate that there is no significant deterioration of water quality between the storage tank and the property boundary. Responsibility is transferred to the property owner at the metered valve at this point.

#### Figure 1: Scheme process flow diagram

### 3.2.5.	Operating environment

Include details of operating conditions specific to the scheme, such as:

- irregular patterns of supply and/or demand, such as seasonal shutdowns

- planned stoppages such as during scheduled maintenance

- partnerships or contractual arrangements, or outsourced services

- alternative water supply arrangements, if relevant.

### 3.2.6.	Recycled water product

This section should identify the recycled water product and the associated water quality objectives, including any required log reduction values (LRV), for each of the intended uses. Evidence should be provided to demonstrate that the proposed water quality is appropriate, and complies with any regulated standards, for the intended uses. This should include references to applicable criteria and standards in the Public Health Regulation 2005 and Water quality guidelines for recycled water schemes, as well as other relevant guidelines, research or industry standards to justify the nominated water quality.

An assessment of relevant existing, or historical data for the scheme should be incorporated if available; for example, data captured via ongoing operational or verification monitoring programs. Control charts can assist in analysing the data to identify trends, abnormal results and any gaps in data. The reliability of the data should also be considered. This provides a characterisation of the quality and variability of recycled water produced by the scheme and may assist in identifying potential hazards and hazardous events that may impact on recycled water quality.

## 3.3.	Hazard identification and risk assessment

The following sections of the RWMP should document the risk assessment process undertaken by the analysis team. Where the scheme has current certification for an existing risk management system, e.g. HACCP, a copy of the certification should be attached, and taken into account when undertaking the risk assessment. The outcomes of the hazard identification and risk assessment process should be incorporated into a summary table, including the identified hazards and hazardous events, unmitigated and residual risk rankings and control measures. An example of such a table is provided in the Risk Assessment table below.

Notes:		Refer to section 3.4 of the RWMP and Validation Guideline

For additional guidance refer to section 2.2.4 and chapter 3 of the AGWR

### 3.3.1.	Methodology

The risk management methodology should be clearly documented in this section. This should include conducting an initial induction to ensure that all members of the risk assessment team have a clear and mutual understanding of the process prior to commencing the assessment.

Different terminology may be relevant, based on the risk management methodology used. Ensure terminology is clearly defined and consistently used in the RWMP. While the specific methodology may vary, the main elements of hazard identification and risk assessment should be addressed, as outlined in the following sections.

### 3.3.2.	Hazard identification

Document the hazards identified at their introduction to the scheme based on the available information, such as the source water characterisation, system description and intended uses.

Depending on the intent and jurisdictional requirements, hazards may relate to human or environmental health or financial impacts. For the purpose of this document hazard identification should focus directly on public health. The most significant human health hazards are likely to be microorganisms capable of causing illnesses, however biological, chemical and physical factors should be considered. Consideration should also be given to variability of potential hazards to ensure seasonal and intermittent hazards are captured.

### 3.3.3.	Hazardous events

Hazardous events, those that may result from or lead to the presence of a hazard, can vary from process failure to human error or unauthorised use of recycled water.

Document the hazardous events identified and their sources or where they may occur in the process.

### 3.3.4.	Unmitigated risks

Record the level of unmitigated risk, also known as maximum risk, estimated for the identified hazards and hazardous events in the absence of any preventive measures. An initial screening-level risk assessment may be used to screen out very low risk hazards, allowing more detailed qualitative or quantitative risk assessment processes to focus on hazards of most relevance to the scheme.

### 3.3.5.	Significant risks

Once all hazards and hazardous events have been assessed in terms of unmitigated risk, the analysis team should agree to and document the cut off for significant risk. The cut off distinguishes between what is and is not considered an acceptable level of risk. Significant risks will determine management priorities and generally be the focus of the critical control points.

### 3.3.6.	Uncertainty levels

Some level of uncertainty is inherent in the estimation of risk. The degree of uncertainty will depend on the variability of the hazard itself within the system, and the comprehensiveness and reliability of available knowledge and data. Understanding the uncertainty associated with hazards may assist in identifying measures that may be implemented to moderate hazard variability, or targeted research to address knowledge deficiencies.

Document the main sources of uncertainty for each hazard and hazardous event to contextualise future risk assessments and inform research and development programs.

### 3.3.7.	Control measures and residual risk

Identify the existing control measures and multiple barriers that prevent significant hazards from being present in the recycled water and hazardous events from occurring, and the subsequent residual risk rankings assigned to each significant risk.

Where the existing measures identified do not sufficiently mitigate significant hazards, alternative and additional control measures should be identified that ensure residual risks are reduced to acceptable levels. Provide detail regarding specific preventive measures and strategies addressing each significant risk. Relevant procedures may be attached to the document if required. For dual reticulation schemes, ensure measures to prevent and control cross connections, such as audit programs, are detailed.

## 3.4.	Operational control

Appropriate mechanisms must be established for managing control measures that are essential in preventing significant hazards or reducing them to acceptable levels. Information in these sections may be summarised in a table.

Notes:		Refer to section 3.5 of the RWMP and Validation Guideline

For additional guidance refer to sections 2.3 and 2.4 of the AGWR

### 3.4.1.	Critical control points

Critical control points (CCPs) are control measures that are essential in removing significant hazards or reducing them to an acceptable level, and for which performance efficacy can be monitored and controlled. Failure of a CCP is likely to require the scheme to be shut down or cease supply until corrective action can be taken.

Quality control points (QCPs) are also important in controlling significant hazards, but are not key mechanisms for assuring effective hazard removal, either because the hazard will be sufficiently mitigated at a subsequent process step, or because performance is not able to be adequately monitored and controlled to enable a timely response to any failures.

Document the critical and quality control points identified throughout the recycled water system and the process used to systematically assess process steps and identify control points, for example the decision tree that was used.

### 3.4.2.	Critical limits

Critical limits define the operational tolerance levels for monitoring the performance of critical processes. Operation within critical limits indicates the process is functioning effectively to remove the relevant hazards and produce water of acceptable quality. Critical limits should be exact values, not a range.

Document the operational monitoring parameters and critical limits identified for each critical control point and the corrective actions required when these limits are deviated from.

### 3.4.3.	Alert levels

Target criteria, alert levels, or early warning systems for the scheme should also be indentified, along with details of corrective actions that will be undertaken in response to deviations from the target criteria to prevent exceedence of critical limits.

Example: Risk assessment

The following example is based on a qualitative risk assessment process using risk matrices from the AGWR. Hazards and associated risk levels will vary greatly from scheme to scheme depending on the source, treatment systems and end use or environmental end point. Identified hazards and risk levels will also vary according to the intent of the risk assessment. This example focuses only on risks to public health and does not consider environmental risk.

#### Qualitative measures of likelihood

| Level | Descriptor | Example description |
| --- | --- | --- |
| A | Rare | May occur only in exceptional circumstances. May occur once in 100 years |
| B | Unlikely | Could occur within 20 years or in unusual circumstances |
| C | Possible | Might occur or should be expected to occur within a 5- to 10-year period |
| D | Likely | Will probably occur within a 1- to 5-year period |
| E | Almost certain | Is expected to occur with a probability of multiple occurrences within a year |

#### Qualitative measures of consequence or impact

| Level | Descriptor | Example description |
| --- | --- | --- |
| 1 | Insignificant | Insignificant impact or not detectable |
| 2 | Minor | Health — Minor impact for small population Environment — Potentially harmful to local ecosystem with local impacts contained to site |
| 3 | Moderate | Health — Minor impact for large population Environment — Potentially harmful to regional ecosystem with local impacts primarily contained to on-site |
| 4 | Major | Health — Major impact for small population Environment — Potentially lethal to local ecosystem; predominantly local, but potential for off-site impacts |
| 5 | Catastrophic | Health — Major impact for large population Environment — Potentially lethal to regional ecosystem or threatened species; widespread on-site and off-site impacts |

#### Qualitative risk estimation

| Likelihood | Consequence |
| --- | --- |
|  | 1 Significant | 2 Minor | 3 Moderate | 4 Major | 5 Catastrophic |
| A Rare | Low | Low | Low | High | High |
| B Unlikely | Low | Low | Moderate | High | Very High |
| C Possible | Low | Moderate | High | Very High | Very High |
| D Likely | Low | Moderate | High | Very High | Very High |
| E Almost certain | Low | Moderate | High | Very High | Very High |

Source: Australian Guidelines for water recycling: managing health and environmental risks (phase1), 2006.

#### Risk assessment

| ID | Source of hazard | Hazard or hazardous event | Potential impact | Unmitigated risk | Preventive measures | Residual risk |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | L | C | R |  | L | C | R |
| 1. Sewage catchment |
| 1.1 | Source water | Bacteria | Illness (chronic or acute) from exposure to recycled water via end uses | E | 4 | Very high | Ultrafiltration, UV/ chlorine disinfection, user controls (signage, communication, restricted access) | B | 2 | Low |
| 1.2 | Source water | Viruses | Illness (chronic or acute) from exposure to recycled water via end uses | E | 5 | Very high | Ultrafiltration, UV/ chlorine disinfection, user controls (signage, communication, restricted access) | B | 2 | Low |
| 1.3 | Source water | Protozoa | Illness (chronic or acute) from exposure to recycled water via end uses | E | 4 | Very high | Ultrafiltration, UV/ chlorine disinfection, user controls (signage, communication, restricted access) | B | 2 | Low |
| 1.4 | Source water | Helminths | Illness (chronic or acute) from exposure to recycled water via end uses | E | 4 | Very high | Ultrafiltration, user controls (signage, communication, restricted access) | B | 2 | Low |
| 1.5 | Source water | High nutrient levels promoting algal growth on membrane filters and in storages | Reduced treatment efficiency; Production of algal toxins | D | 2 | Moderate | Biological treatment, clarification, NaOCl dosing at membrane feed | B | 1 | Low |
| 1.6 | Source water | High or low pH affecting biological treatment systems and reducing chlorine efficacy | Reduced treatment efficiency; Ineffective disinfection | C | 3 | High | Monitoring of source water pH prior to inlet works and pH adjustment as necessary | A | 2 | Low |
| 1.7 | Source water | High level of solids resulting in overloading of membranes and ineffective disinfection | Reduced treatment efficiency | E | 4 | Very high | Primary treatment, biological treatment, ultrafiltration | B | 2 | Low |
| 1.8 | Source water: Commercial/ industrial discharge | Heavy metals Industrial chemicals Pesticides | Illness (chronic or acute) from exposure to recycled water via end uses Reduced health of biological treatment systems | D | 3 | High | Trade waste agreements with commercial/industrial producers, source water monitoring, absorption by biological treatment system | B | 2 | Low |
| 1.9 | Illegal trade waste discharge | Heavy metals Industrial chemicals Pesticides | Illness (chronic or acute) from exposure to recycled water via end uses Reduced health of biological treatment systems | D | 2 | Moderate | Source water monitoring, auditing of trade waste generators in accordance with NRC’s trade waste program, absorption by biological treatment system | C | 1 | Low |
| 1.10 | Extreme wet weather event | Hydraulic overload of treatment systems | Reduced treatment efficiency | C | 3 | High | Balance tank, emergency bypass | C | 1 | Low |
| 2. Balance tank |
| 2.1 | Failure at balance tank (e.g. valve or pump) | Hydraulic overload of treatment systems | Reduced treatment efficiency | B | 2 | Low | Scheduled equipment maintenance, emergency bypass | A | 1 | Low |
| 3. Inlet works |
| 3.1 | Screen failure | Gross solids damaging treatment systems | Reduced treatment efficiency | B | 3 | Moderate | Equipment inspection and maintenance, standby screen, emergency bypass | A | 1 | Low |
| 4. Bioreactor |
| 4.1 | Insufficient activated sludge mass resulting in ineffective biological treatment | Excess nutrients and organic matter resulting in overloading of membranes and ineffective disinfection | Reduced treatment efficiency | C | 2 | Moderate | Monitoring of sludge age, online monitoring of ammonia at outlet of aerobic chamber | B | 2 | Low |
| 4.2 | Insufficient aeration of aerobic chamber | Excess nutrients and organic matter resulting in overloading of membranes and ineffective disinfection | Reduced treatment efficiency | C | 2 | Moderate | Online monitoring of DO | B | 2 | Low |
| 5. Clarifier |
| 5.1 | Ineffective sludge removal | High level of solids resulting in overloading of membranes and ineffective disinfection | Reduced treatment efficiency | B | 4 | High | Online turbidity monitoring of clarified effluent, alarming and manual diversion | B | 1 | Low |
| 6-8 Class C only |
| 6. Chlorine contact tank (Class C) |
| 6.1 | Underdosing of chlorine resulting in inadequate disinfection | Pathogenic microorganisms (bacteria, viruses) | Illness from exposure to out-of-spec recycled water | C | 3 | High | Online monitoring of chlorine residual, scheduled equipment calibration and maintenance | B | 2 | Low |
| 6.2 | Insufficient contact time resulting in inadequate disinfection | Pathogenic microorganisms (bacteria, viruses) | Illness from exposure to out-of-spec recycled water | C | 3 | High | Online monitoring of chlorine residual and flow rate | B | 2 | Low |
| 6.3 | High or low pH resulting in inadequate disinfection | Pathogenic microorganisms (bacteria, viruses) | Illness from exposure to out-of-spec recycled water | B | 4 | High | pH monitoring at feed to CCT | A | 3 | Low |
| 7. Class C storage |
| 7.1 | Regrowth of pathogens | Pathogenic microorganisms | Illness from exposure to out-of-spec recycled water | C | 3 | High | Limited storage period, monitoring and maintenance of chlorine residual | B | 2 | Low |
| 7.2 | Contamination of storage from an external source (e.g. wildlife, sabotage) | Pathogenic microorganisms Chemical | Illness from exposure to out-of-spec recycled water | C | 3 | High | Sealed storage, limited access, routine inspection and maintenance of storage, maintain chlorine residual, monitoring of final water quality | B | 2 | Low |
| 7.3 | Algal growth | Algal toxins | Illness from exposure to toxins in recycled water | C | 2 | Moderate | Nutrient removal through biological treatment, sealed storage limiting light, user controls | B | 2 | Low |
| 8. End uses (Class C) – open space irrigation |
| 8.1 | Accidental or intentional ingestion from recycled water taps (unplanned use) | Pathogenic microorganisms Chemical | Illness from exposure to hazards via ingestion of in-spec recycled water | D | 4 | Very high | Signage, locked valves on recycled water taps | A | 3 | Low |
| 8.2 | Ingestion of spray during irrigation | Pathogenic microorganisms Chemical | Illness from exposure to hazards via ingestion of in-spec recycled water | D | 2 | Moderate | Irrigation at night, controlled access, signage | B | 2 | Low |
| 8.3 | Contact with irrigated turf | Pathogenic microorganisms Chemical | Illness from exposure to hazards via skin contact | E | 2 | Moderate | Irrigation at night allowing for withholding period | C | 1 | Low |
| 8.4 | Over-irrigation resulting in ponding of recycled water | Pathogenic microorganisms Chemical | Illness from exposure to hazards via skin contact | C | 2 | Moderate | Irrigation at night allowing for withholding period | B | 2 | Low |
| Continues from 5 (Clarifier) – Class A+ only |
| 9. Fine screen |
| 9.1 | Screen failure | High suspended solids | Excess solids entering UF units leading to membrane damage and reduced treatment efficiency | C | 3 | High | Routine inspection and maintenance; Turbidity monitoring prior to UF, automatic shutdown of feed pump in event of exceedence of critical limits | B | 1 | Low |
| 10. Ultrafiltration |
| 10.1 | Membrane breakthrough | Pathogenic microorganisms | Illness from exposure to out-of-spec recycled water | B | 4 | High | Online monitoring of turbidity, pressure decay testing, alarming. Standby membrane (rotational) Routine inspection and maintenance | B | 1 | Low |
| 10.2 | Excessive flux | Reduced performance from overloading of membrane | Reduced treatment efficiency | C | 3 | High | Flow (flux) monitoring post-filtration TMP monitoring | B | 2 | Low |
| 11. UV disinfection |
| 11.1 | Failure of 1 or more units resulting in inadequate disinfection | Pathogenic microorganisms (bacteria, viruses, protozoa) | Illness from exposure to out-of-spec recycled water | C | 3 | High | Dose monitoring; Routine equipment calibration and maintenance; Redundancy (can meet minimum objective with one unit offline) | B | 2 | Low |
| 11.2 | High turbidity shielding pathogens resulting in inadequate disinfection | Pathogenic microorganisms (bacteria, viruses, protozoa) | Illness from exposure to out-of-spec recycled water | B | 3 | Moderate | Turbidity monitoring post-filtration | A | 3 | Low |
| 12. Chlorine contact tank (Class A) |
| 12.1 | Underdosing of chlorine resulting in inadequate disinfection | Pathogenic microorganisms (bacteria, viruses) | Illness from exposure to out-of-spec recycled water | C | 3 | High | Online monitoring of chlorine residual, scheduled equipment calibration and maintenance | B | 2 | Low |
| 12.2 | Overdosing of chlorine | High chlorine residual, disinfection byproducts | Exposure to potential carcinogens | C | 1 | Low | Online monitoring of chlorine residual, scheduled equipment calibration and maintenance | B | 1 | Low |
| 12.3 | Insufficient contact time resulting in inadequate disinfection | Pathogenic microorganisms (bacteria, viruses) | Illness from exposure to out-of-spec recycled water | C | 3 | High | Online monitoring of chlorine residual and flow rate | B | 2 | Low |
| 12.4 | High or low pH resulting in inadequate disinfection | Pathogenic microorganisms (bacteria, viruses) | Illness from exposure to out-of-spec recycled water | C | 3 | High | pH monitoring at feed to CCT | B | 2 | Low |
| 13. Class A+ storage |
| 13.1 | Regrowth of pathogens | Pathogenic microorganisms | Illness from exposure to out-of-spec recycled water | C | 3 | High | Limited storage period, monitoring and maintenance of chlorine residual | B | 2 | Low |
| 13.2 | Contamination of storage from an external source (e.g. wildlife, sabotage) | Pathogenic microorganisms Chemical | Illness from exposure to out-of-spec recycled water | C | 3 | High | Sealed storage, limited access, routine inspection and maintenance of storage, maintain chlorine residual, monitoring of final water quality | B | 2 | Low |
| 13.3 | Algal growth | Algal toxins | Illness from exposure to toxins in recycled water | C | 2 | Moderate | Nutrient removal through biological treatment, sealed storage limiting light, monitoring of final water quality, user controls | B | 2 | Low |
| 14. End use (Class A+) – irrigation of minimally processed food crops |
| 14.1 | Cross-connection (accidental) with potable source | Pathogenic microorganisms Chemical | Illness from ingestion of in-spec recycled water (high exposure, may be long-term) | C | 4 | Very high | Colour coding of recycled water pipes and fixtures (purple), conductivity testing following installation | A | 2 | Low |
| 14.2 | Accidental or intentional direct ingestion | Pathogenic microorganisms Chemical | Illness from exposure to hazards via ingestion of in-spec recycled water | D | 3 | High | All employees and visitors to property informed regarding appropriate use of recycled water, colour coding of fixtures, signage | A | 2 | Low |
| 14.3 | Ingestion of spray from irrigation by workers, passers-by and near-by residents | Pathogenic microorganisms Chemical | Illness from exposure to hazards via ingestion of in-spec recycled water | D | 2 | Moderate | Signage, irrigation at night | B | 2 | Low |
| 14.4 | Over-irrigation resulting in ponding of recycled water | Pathogenic microorganisms Chemical | Illness from exposure to hazards via skin contact | C | 1 | Low | Signage, irrigation at night | B | 1 | Low |

#### Critical control points

To identify Critical Control Points (CCPs) and Quality Control Points (QCPs), each process step within the system was assessed with respect to significant hazards (those with an unmitigated risk of moderate to very high) using the following decision tree adapted from the AGWR. The results of the CCP and QCP identification process are outlined in Table X.

#### Table X: CCP and QCP identification

| Process step | Decision Tree | CCP or QCP? |
| --- | --- | --- |
|  | Q1 | Q2 | Q3 | Q4 |  |
| 1. Sewage catchment | Y | Y | N |  | QCP |
| 2. Balance Tank | Y | N |  |  | No |
| 3. Inlet works | Y | N |  |  | No |
| 4. Bioreactor | Y | Y | Y | Y | CCP |
| 5. Clarifier | Y | Y | Y | N | QCP |
| 6 Chlorine Contact Tank (Class C) | Y | Y | Y | Y | CCP |
| 7. Storage (Class C) | Y | Y | Y | N | QCP |
| 8. End uses (Class C) | Y | Y | N |  | QCP |
| 9. Fine screen | Y | Y | Y | Y | CCP |
| 10. Ultrafiltration | Y | Y | Y | Y | CCP |
| 11. UV Disinfection | Y | Y | Y | Y | CCP |
| 12. Chlorine Contact Tank (Class A+) | Y | Y | Y | Y | CCP |
| 13. Storage (Class A+) | Y | Y | Y | N | QCP |
| 14. End use (Class A+) | Y | Y | N |  | QCP |

#### Monitoring of critical control points

| CCP | Parameter monitored | Location | Alert level | Critical limit | Corrective actions |
| --- | --- | --- | --- | --- | --- |
| Bioreactor | Ammonia Nitrate | Aerobic chamber Aerobic chamber | > 2.5 mg/L > 5 mg/ | > 3.5 mg/L > 8 mg/L | Check DO monitoring results from aerobic chamber to ensure adequate aeration; check sludge age and adjust as necessary May require screening of source water for potential industrial toxicant contamination |
| Fine Screens | Turbidity | Ultrafiltration feed | >2 NTU | >5 NTU | Automatic shutdown of feed pump to ultrafiltration units Inspection and action in accordance with operational procedures |
| Ultrafiltration | Pressure decay testing (daily) Flux Filtrate turbidity | Membrane units Membrane units Post membrane units | PDR >3 kPa/min >30 L/m2.h > 0.5 NTU | PDR >5 kPa/min >38 L/m2.h >1 NTU | Switch duty/standby trains. Inspection and repair in accordance with operational procedures. Breach of CL’s at multiple units will result in shutdown of feed pump to ultrafiltration units |
| UV Disinfection | Dose intensity UV transmissivity | UV units | <70 mJ/cm2 <90% for 10mins | <60 mJ/cm2 <85% for 1hour | Inspection and action in accordance with operational procedures |
| Chlorine Contact Tank (Class C & Class A+) | pH (online) Free chlorine residual (online) | Pre-CCT Outlet from chlorine contact tank | >7.5 ≥ 5 mg/L ≤ 0.7 mg/L | >8.5 ≥ 7 mg/L ≤ 0.2 mg/L | pH adjustment as necessary. Investigate cause Inspect chlorine dosing system, monitoring equipment for faults Adjust dose as required |

# 4.	Scheme validation

Validation is the process of proving that the recycled water system will be capable of consistently achieving the performance objectives and meeting the minimum water quality criteria identified for the scheme. Typically, validation is undertaken at the pre-commissioning and commissioning stages of the scheme’s operation, before supply to end users has commenced. Revalidation may need to occur at later stages in response to significant changes to the scheme or operating conditions (refer to 4.2. below).

The RWMP and Validation Guideline addresses three phases of validation:

- pre-commissioning validation – generally undertaken during the planning and design stage to determine the combination of treatment components that will be required to meet the required water quality

- commissioning validation – confirms that selected components perform as expected when operating as part of the treatment system

- commissioning verification – testing of final product water to show that the system as a whole produces the expected water quality

Within these phases, there are numerous validation methodologies that may be used to demonstrate system performance. Appropriate methodologies will depend on the type and complexity of scheme, the chosen technologies and hazards being addressed. Section 3.6 of the RWMP and Validation Guideline details the main types of validation and provides a ‘points system’ as a guide to suitable combinations of validation methods for different scheme types.

Existing schemes (those that were in operation prior to commencement of the Act in July 2008) that have substantial existing data may only need to provide verification (final water quality monitoring) results that demonstrate that the scheme has been consistently producing the required water quality.

Note:	Refer to section 3.6 of the RWMP and Validation Guideline

## 4.1.	Validation program

The validation program documents how the performance of the recycled water scheme will be assessed. It contains information about the methodology to be used to validate each component, as well as the system as a whole.

Schemes supplying recycled water for augmenting drinking water supplies are required to submit the proposed validation program for approval by the regulator prior to applying for approval of the RWMP. For other types of schemes the validation program is submitted with the RWMP application.

Outcomes from the validation program should be incorporated into the detail of the RWMP for all schemes.

### 4.1.1.	Validation of treatment processes

Document the process for validating the individual treatment processes that contribute to the required water quality objectives. Although the methodology may vary, for each process the following should be addressed:

- indentify target pathogens

- specify log reduction requirement

- identify the methodology to be used to demonstrate log reduction

- provide analysis of data or evidence to show that the required log reduction can be achieved.

### 4.1.2.	Verification of final water quality

As well as individually validating process units, results of final water quality monitoring should be assessed to confirm that overall system performance is adequate to meet the water quality criteria (commissioning verification).

### 4.1.3.	Validation of critical limits, operational limits and corrective actions

In conjunction with validation of treatment processes and final water quality, critical limits and associated corrective responses should be validated to demonstrate that:

- the system is capable of consistently operating within the set limits

- the limits effectively indicate the corresponding control measure is performing at a level to achieve the required hazard removal

- operating within critical limits ensures recycled water quality criteria are met at the verification step.

Demonstrate that the critical limits, operational limits and corrective actions can be consistently achieved, and are set at a level appropriate to ensure the required treatment performance.

### 4.1.4.	Validation report

The validation program should be documented in a report that details the following for each item being validated; this may be in a separate report appended to the RWMP:

- the aim of the validation

- the methodology used

- the results of the validation undertaken

- the conclusion of the validation, that is, whether the aim of the validation was met

- a summary of outcomes from the validation program.

## 4.2.	Revalidation

Throughout the life of the scheme, significant changes to operating conditions or processes may occur that necessitate revalidation of individual processes and the system as a whole to ensure that water quality objectives can still be consistently achieved under the altered conditions.

Document scenarios that may occur that will trigger revalidation of systems or processes. Types of changes to the scheme that may be considered include:

- source water quality or catchment changes, e.g. new or increased concentrations of hazards detected; or a new industrial development in the sewage catchment

- upgrades or changes to infrastructure or processes, such as treatment components, chemicals, critical limits or operating parameters; plant capacity

- audits or reviews indicating ongoing compliance issues

- new intended end uses requiring more stringent water quality standards

- changes to legislation, water quality criteria or industry standards.

# 5.	Operational procedures and process control

This section should document the procedures for ensuring system processes and activities occur effectively and correctly to produce recycled water of acceptable quality. This information may be formalised in the organisation’s operating procedures which should be described and referenced in the RWMP where applicable.

## 5.1.	Operational procedures

Operational procedures should describe process control programs for the scheme. These may be compiled in an operation manual which could be an attachment to the RWMP. Document the positions responsible for the activities in the procedures and how staff are trained in the procedures.

## 5.2.	Source water monitoring

Characterisation of source water should be ongoing to account for changes over time, and assist identification of new or emerging hazards. Parameters and monitoring frequencies should be risk based.

Provide details of the ongoing source water monitoring program.

## 5.3.	Operational monitoring

Provide a plan that details the operational monitoring protocols, including:

- responsible personnel

- operational monitoring parameters

- criteria or performance targets

- monitoring frequency

- analysis of results to determine operational efficacy.

## 5.4.	Operational corrective actions

Include procedures for corrective actions which establish process control, immediately when critical limits or target criteria are exceeded. These may be included as part of the operational procedures for the scheme or as separate corrective procedures.

Include the responsibilities for actions in procedures, and how reviews will occur after corrective actions are taken.

### 5.4.1.	Communication systems

Document the communication systems to be implemented when process control is lost, including the responsibilities for executing communication protocols.

## 5.5.	Monitoring equipment

Equipment used for operational monitoring needs to be capable and suitable for the monitoring task. Consequently, maintenance of the monitoring equipment is critical in the provision of consistent and reliable results and performance.

### 5.5.1.	Equipment maintenance

Provide details of the maintenance requirements for the equipment and infrastructure used in the scheme. Detail the responsibility for scheme and process maintenance. This information may be available in the manufacturer’s specification and summarised in an organisation’s maintenance schedule.

# 6.	Verification of recycled water quality and operational performance

This section will document details of ongoing verification of final water quality.

## 6.1.	Recycled water quality monitoring

Include the ongoing verification monitoring program for the scheme that will demonstrate final water quality meets required standards.

### 6.1.1.	Monitoring location(s)

Document the location(s) in the scheme where verification monitoring will occur. The monitoring point(s) may have regulatory implications, for example in jurisdictions where final water quality is regulated the monitoring point(s) should be representative of the final water quality. In other instances a monitoring point might be linked to sale agreements that define the water quality for a specific use. Similar to meeting regulatory requirements, these monitoring point(s) should also be indicative of final water quality.

### 6.1.2.	Monitoring parameters

List the characteristics to be monitored and process for selection, including demonstration that they are adequate/efficient indicators of final water quality. In jurisdictions where final recycled water quality is regulated some parameters may be predetermined. Demonstrate that the chosen parameters meet regulatory requirements.

### 6.1.3.	Monitoring frequency

Describe and justify the frequency of monitoring for the identified verification monitoring parameters. In jurisdictions where final recycled water quality is regulated some frequencies may be predetermined. Demonstrate that the chosen frequencies meet regulatory requirements.

### 6.1.4.	Sampling techniques

Provide details of procedures for the collection and handling of samples, including how samples are taken, who is responsible and the training provided to responsible personnel.

### 6.1.5.	Sample analysis

Provide details of the facilities used to undertake analysis of samples. Ideally sample analysis should be performed by a laboratory with NATA (National Association of Testing Authorities) accreditation for the relevant analysis procedures. Where a NATA accredited laboratory is not used, documentation should be provided that details the methodology, including quality assurance and quality control procedures, used to perform the analysis.

| Example: Verification monitoring program Verification monitoring is carried out at the final water quality monitoring points as shown in the process flow diagram in Figure 1, at the outfall of the class A+ and class C recycled water storage tanks. Sample analysis is undertaken at the NRC NATA accredited laboratory. The parameters and frequency are in accordance with standards for class A+ and class C recycled water in the Public Health Regulation 2005 as follows: Final water quality monitoring (Class A+) |
| --- |
| Parameter | Frequency |
| Clostridium perfringens | Weekly |
| Escherichia coli | Weekly |
| F-RNA bacteriophages | Weekly |
| Somatic coliphages | Weekly |
| Turbidity | Daily |
| Final water quality monitoring (Class C) |
| Parameter | Frequency |
| Escherichia coli | Weekly |

## 6.2.	Documentation and reliability

The verification monitoring program should identify the processes for establishing reliability of the data. Roles and responsibilities, sampling and analysis methodologies, record keeping and details of equipment calibration should be included. Evidence may be attached for third party certification of management systems under a relevant standard, e.g. AS/NZS ISO 9001.

## 6.3.	Satisfaction of recycled water users

Include a user complaints and response program. The roles and responsibilities should be identified in the program. The program should identify the process for documenting complaints and responses.

Example: Satisfaction of recycled water users Customer complaints are received at the NRC Customer Service Centre. Customer service officers record details in the Complaint Received form (attached in Appendix X), which includes the name and contact details of the complainant and nature of the complaint, and the form is forwarded immediately by email to the water services division for action. Details of all complaints, including investigations, follow-up actions and resolution, are recorded by the action officer in the Register of Complaints.

## 6.4.	Short-term evaluation of results

Detail the process for reviewing and evaluating verification monitoring data and user complaints to ensure better scheme management. Document mechanisms for communication and reporting of results, both internally and externally. This may be part of a broader scheme performance evaluation procedure.

## 6.5.	Corrective responses

Include procedures for corrective responses, including the analysis of operational procedures and monitoring in response to verification monitoring and user complaints. Ensure communication and reporting protocols are established.

# 7.	Management of incidents and emergencies

There should be a documented system for managing and responding to incidents and emergencies that might occur during operation of the scheme. The following sections may be covered in an incident and emergency response plan developed for the scheme, attached to the RWMP.

## 7.1.	Communication

Provide communication protocols that in the event of an incident or emergency will facilitate communication with relevant entities, including:

- relevant agencies, including emergency response and regulatory bodies

- end users

- public and media.

## 7.2.	Incident and emergency response protocols

Document the potential incidents and emergencies which may occur and the relevant response plans. Establish response actions and responsibilities. Identify the training requirements for staff involved in the execution of the protocols.

### 7.2.1.	Continuous improvement of incident management

The incident and emergency protocol should identify how management of incidents and emergencies will be investigated, documented, reported and evaluated for continuous improvement of both incident response processes, and preventive measures.

# 8.	Documentation management and reporting

Provide systems for document management and reporting. Where electronic systems are used, summarise their attributes and functionalities that ensure adequate document management and record keeping.

## 8.1.	Management of documentation and records

Include a procedure or system that provides for the management of documentation and records, including operational and verification monitoring data. This should include a method for document control, how records will be kept for easy access and integrity retention, and how staff will be trained to use systems efficiently.

## 8.2.	Document review

Provide a summary of how often documents and systems will be periodically reviewed.

Example: Document review A regular review of the RWMP will be conducted at least every year to ensure the RWMP remains relevant having regard to: the operation of the recycled water scheme the water quality criteria for recycled water relevant to the scheme best practice industry standards for the production and supply of recycled water. If the review indicates the plan should be changed, NRC will amend the RWMP to reflect the findings of the review and apply to the regulator for approval of the amended plan. Otherwise, findings of the review will be incorporated into the annual report for that year.

## 8.3.	Reporting

Include procedures for effective internal and external reporting, including annual reporting, community/public reporting and regulator reporting.

# 9.	Supporting programs

## 9.1.	Operator, contractor and end user awareness and training

Include an awareness and training program for operators, contractors and end users. This may be in the form of procedures attached to the RWMP as reference documents.

### 9.1.1.	Operator, contractor and end user awareness and involvement

Document mechanisms and communication procedures which increase awareness and participation in water quality management, protection of public health, and environmental protection.

### 9.1.2.	Operator, contractor and end user training

Describe the training requirements for operators, contractors and users for the different aspects of the scheme. Document the skills and experience required by operators and contractors.

## 9.2.	End user agreements

Provide details, and if possible attach copies, of formal agreements or contracts with end users under the scheme that ensure that recycled water is used appropriately, as provided for in the RWMP, and that on-site control measures are implemented as required.

## 9.3.	Community involvement and awareness

### 9.3.1.	Consultation

Describe the process for consultation with recycled water users and the community, including the strategies that were used and how consultation was incorporated into the development of the scheme.

### 9.3.2.	Communication and education

Provide a two-way communication program used to raise awareness, and inform the community on the scheme and the use of recycled water. Schemes providing recycled water for dual reticulation must provide details of an education and risk awareness program, as outlined in section 4 of the RWMP and Validation Guideline.

## 9.4.	Evaluation and audit

Document the process for long-term data collection and how it will be used to assess performance and identify problems.

### 9.4.1.	Audit of recycled water quality management

Provide a process for internal and external audits, including frequencies, roles and responsibilities and the process for documenting and reporting results. Additionally, outline any triggers that may result from audit results (for example changes to the scheme, the RWMP or other documents).

Example: Auditing Internal audits will be conducted annually by NRC staff members who, as a minimum, have completed a two day audit training course. A regular external audit of the RWMP will be conducted by a suitably qualified independent auditor (not an employee of NRC) at least every three years. Internal and external audits will assess compliance with the RWMP and conditions of approval. Audit reports will be reviewed by the Manager of Water Services and if the report indicates compliance issues, the analysis team will be convened to determine appropriate action. Actions potentially triggered by audit findings include: review of the RWMP, and amendment if necessary revalidation of treatment processes and critical limits review of risk assessment process review of management systems and procedures. Audit results and reports are submitted to the approval agency and retained in accordance with document management procedures.

## 9.5.	Review and continuous improvement

Document the review and continuous improvement mechanisms that will be undertaken for the scheme. This should include roles and responsibilities, the documentation and communication of results and the involvement of senior management. Document the processes that may be triggered by reviews, for example commencement of a recycled water quality management improvement plan.

# 10.	References

# 11.	Appendices

# Footnotes

Development of a Recycled Water Management Plan in accordance with the Water Supply (Safety and Reliability) Act 2008

# Text boxes

Insert publication number

Insert publication number

The Department of Primary Industries and Fisheries (DPI&F) seeks to maximise the economic potential of Queensland's primary industries on a sustainable basis.

© The State of Queensland, Department of Primary Industries and Fisheries, 2008. 

Except as permitted by the Copyright Act 1968, no part of the work may in any form or by any electronic, mechanical, photocopying, recording,or any other means be reproduced, stored in a retrieval system or be broadcast or transmitted without the prior written permission of DPI&F. The information contained herein is subject to change without notice. The copyright owner shall not be liable for technical or other 
errors or omissions contained herein. The reader/user accepts all risks and responsibility for losses, damages, costs and 
other consequences resulting directly or indirectly from using this information. 

Enquiries about reproduction, including downloading or printing the web version, should be directed to ipcu@dpi.qld.gov.au or telephone +61 7 3225 1398.

Insert report title here

Insert subtitle